ANNEXURE 1: SPECIFICATION OF WORK

Overall Statement of Work

The work associated with this tender can be summarised as the detailed design finalisation, construction, installation and commissioning of the Storage Facility and the installation and commissioning of the integrated Environmental and Radiation Monitoring System (ERMS), with Electrical Supply System (ESS), on this site in accordance with the provided technical design specifications. In this regard:

- The provided technical design packages of the Storage Facility need to be verified, integrated, and finalised for construction, and all relevant documentation for design verification and construction authorisation needs to be prepared, including detailed cost estimates and plans for establishment of the facility.

- All items (goods) of the Storage Facility and ERMS, excluding the IMP, need to be procured and verified and validated (as applicable) for conformance with the final design specifications, and records of site acceptance (conformance to design specifications) of these items (goods) need to be provided.

- The Storage Facility needs to be constructed and verified for conformance to the final design specifications, and all relevant construction documentation (e.g., construction report, construction and materials certificates, change management records, functional testing reports, etc.) need to be provided.

- The sub-systems of the Storage Facility need to be installed and verified/validated for conformance to the final design specifications and in accordance with the requirements of GD 285 dated 23-05-1996.

- The ERMS needs to be installed, commissioned, and verified and validated for conformance to the final design specifications. Specific systems/items/equipment of the ERMS also need to be certified, qualified and/or accredited as required. (Note that the Radiation Monitoring System of the Storage Facility also forms part of the ERMS).

- The operational manuals and procedures associated with the operation, maintenance and calibration (as applicable) of the Storage Facility and ERMS systems and equipment/instruments need to be developed, and Beneficiary staff need to be trained and certified to operate, maintain and calibrate (as applicable) the Storage Facility and ERMS subsystems, and equipment/instruments (as applicable).

A summary of the main activities associated with establishing the ERMS is provided in Table 1 below to improve understanding of that part of the work associated with the tender.

Table 1: Main Activities Associated with Establishing the ERMS.

| Element | Procurement | Installation | Commissioning / Testing | Lab. Equipment & Analyses | Procedures | Certification / Qualification |
| --- | --- | --- | --- | --- | --- | --- |
| Workplace monitoring | Equipment (portable and fixed) | Yes | Yes | Yes | Yes | Calibration only. |
| Liquid discharge monitoring | Sampling equipment | - | - | Yes | Yes | Accredited Laboratory. |
| Gaseous discharge monitoring | Sampling equipment | Yes | Yes | Yes | Yes | Accredited Laboratory. |
| Environmental monitoring | Drilling of boreholes, equipment, sampling equipment | Yes | Yes | Yes | Yes | Accredited Laboratory. |
| Data recording | Equipment/ Software | Yes | Yes | - | Yes | - |
| Electrical Supply System | Equipment | Yes | Yes | - | Yes | Electrical CoC. |

Brief descriptions (overviews) of the Storage Facility and the ERMS (with ESS) are provided in Sections 2 and 3 respectively, while the project tasks are defined in more detail in Section 6.

Overview of the Storage Facility

General

The facility and its subsystems and equipment are described in the design documentation provided as Annexures 3 and 4 (Table 3). The intermediate storage facility is designed to store packaged solid radioactive waste for a period of up to 50 years. The radioactive waste resulted, in particular, from the decommissioning and remediation of the RADON type facility in the Republic of Moldova, and from industrial, medical, agricultural and research applications (that is mainly associated with low levels of radioactivity).

The waste to be received at the intermediate storage facility has been conditioned and/or (re)packaged at the radioactive waste conditioning facilities of "Special Objects 5101 and 5102". Only conditioned solid waste, containerized in drums or metal containers (the vast majority being packaged in drums), will be accepted for storage at the facility when compliant with the Waste Acceptance Criteria (WAC).

The storage area has been designed so that all types of packages are stored in a safe condition and in compliance with the radiation protection rules on the maximum permitted dose rates and dose constraints applicable to the operating staff and members of the public. The storage area enables the storage of waste packages in three tiers (using support frames for most packages) that are suitably spaced to allow inspection as well as retrieval to implement corrective measures (when deficiencies are detected) or to be transferred to the disposal site.

Facility

The above-ground storage facility has an external concrete platform to provide access for transport vehicles and emergency vehicles/utilities (e.g., fire trucks, etc.), and to facilitate the installation of support systems such as the ventilation system. The platform will be located close to the existing exploration road and be joined to it via an access road. The main components of the facility are:

- Storage area;

- Reception area;

- Administrative area (consisting of locker room, waste package registration desk, vestibule, dosimetry equipment room, packing/storage room, waste parcel handling equipment);

- Ventilation area.

The overall dimensions of the building of the intermediate storage facility are:

- Width of 18.85 m for the storage and reception areas, and width of 23.70 m for the administrative and central ventilation areas;

- Length of 44.30 m;

- Free height of the roof at 11.75 m for the storage areas and at 6.20 m for the technical areas of the facility, which includes the administrative and central ventilation areas.

Three types of waste containers will be accepted at the facility, these are:

- Small metal drums with a volume of 220 L.

- Large metal drums with a volume of 420 L.

- Metal containers with a volume of 1000 L.

The dimensions of these containers, and the number of waste packages associated with these containers considered for storage at the facility are defined in Table 1 below.

Table 2: Waste Package Specifications and Number to be stored.

| PACKAGE TYPE / MAX. LOAD (KG) | DIMENSIONS (MM) | NO. OF PACKAGES |
| --- | --- | --- |
| 220 L Drum / 700 kg | ɸ 645 x 930 | 576 |
| 420 L Drum / 1100 kg | ɸ 755 x 1150 | 144 |
| 1 m3 Container / 3000 kg | 1000 x 1000 x 1000 | 30 |

Subsystems

Ventilation System

The Storage Facility is equipped with a ventilation system that supplies fresh air at four air changes per hour, maintains the temperature and humidity to defined levels, and which keeps the storage area at a slightly negative pressure relative to atmospheric pressure. The ventilation system is switched on prior to personnel entering the facility but operates in automatic mode when no personnel are present to control the humidity and/or temperature in the storage area.

Waste Package Handling Facilities, including Gantry Crane

The Storage Facility is equipped with a gantry crane, electrical forklifts, and auto-elevating platform to ensure the safe handing, placement, transfer, and inspection of waste packages.

Water Supply System and Discharge of Potentially Radioactive Liquid Effluent

Water is supplied to the storage facility changeroom basins for hand-washing using a water container, while waste water is collected in a waste water container. Waste water is analysed for radioactivity content for subsequent discharge or treatment as radioactive effluent. No other supply of water to the facility is envisaged.

Drainage System for Potentially Radioactive Effluents

The floor of the waste reception area of the storage facility is sloped for drainage and collection of liquid in a sump feeding to a collection container. Collected water will be analysed for radioactivity content for subsequent discharge or treatment as radioactive effluent.

Electrical System

The Storage Facility will be connected to an electrical power supply to power the Ventilation System, the gantry crane and lifting equipment, lighting and grounding, power sockets for various equipment, the Low Voltage Systems, and the Radiation Monitoring System.

Low Voltage System

The Low Voltage System that will be installed in the Storage Facility is dedicated to power the following subsystems:

- Fire Detection and Signalling System, that includes as minimum:

  - Optical smoke detectors;

  - Fire signalling buttons;

  - Fire siren with strobe, visible from the inside;

  - Fire siren with strobe, visible from the outside;

  - Fire central, which will be mounted in the Low Voltage System box/rack located in the Room with devices for dosimetry (in the administrative area).

- Voice data system.

- Access control and intrusion detection system.

Automation System

A level indicator is provided for signalling the maximum level in the sump where potentially radioactive effluents are collected from the storage area of the facility. The ventilation system will be installed with fully integrated automation to enable optimal functioning and maintain key operational parameters.

Radiation Monitoring System

The monitoring of the work areas and personnel will be carried out with portable and installed equipment.

Fire Extinguishing System

The Storage Facility is equipped with a fire detection system with fire detectors in all the rooms of the facility, which will, when activated, send alarm signals to the outdoor sirens of the facility.

Overview of the Environmental and Radiation Monitoring System

General

The ERMS is an integrated system that enables the following:

- Workplace monitoring.

- Liquid discharge monitoring.

- Gaseous (emissions) discharge monitoring.

- Environmental monitoring.

- Data recording.

An overview of the subsystems/functions of the ERMS are provided in the subsequent subsections. Refer to the technical design documentation listed in Section 3 for detailed descriptions and specifications of these systems.

Workplace Monitoring

A workplace monitoring programme will be implemented with portable and installed equipment for the following:

- Routine monitoring in accordance with established programmes.

- Operational monitoring during operational activities and whenever activities with enhanced radiation levels and hazards to personnel are conducted.

- Monitoring to detect any changes in radiological conditions.

The following measurements will be taken:

- Gamma and beta dose rates using portable monitors.

- Airborne contamination levels using advanced fixed aerosol sampling systems with integrated alpha/beta/gamma detection, real-time spectrometric analysis, AI-assisted nuclide identification, and automatic Radon/Thoron compensation, supplemented by portable air sampling equipment with laboratory analysis..

- Surface contamination levels of work surfaces, equipment and machinery using portable contamination monitors, smear samples, and laboratory counting and analysis.

- Radon concentration levels in the air with portable equipment.

In order to prevent the spread of radioactive contamination and to detect contamination, radiological zones (controlled areas) need to be identified and be equipped with the following:

- Personnel control points and sanitary gate between different classes of radiological zones (at the interface between areas with different probabilities of contamination). The sanitary gate will be implemented as a purpose-built modular container (ecluză sanitară) serving as a mandatory contamination control facility between the Controlled Zone and Supervised Zone, with unidirectional flow control, integrated monitoring equipment, decontamination facilities, and compliance with national radiation protection requirements (detailed specifications in FT-7).Contamination monitors for personnel (detailed specifications in FT-1)

- Change rooms and facilities (e.g., washbasins, showers, lockers for personal protection equipment and clothing, etc.).

- Portable monitors and detectors at vehicle entrance points to radiological zones (controlled areas).

Fixed Aerosol Sampling Systems will be installed in areas where radioactive materials are handled or where emissions are discharged. The system comprises two types of monitoring equipment:

Type A - Standard Interior Monitoring (4 units): Installed in the Waste Treatment Facility (3 locations) and Long-term Source Storage Facility (1 location). These systems provide continuous monitoring of airborne contamination in work areas with adjustable flow rates (1-7 m³/h), automatic filter changing, and integrated alpha/beta/gamma detection with real-time analysis capabilities (specifications per FT-3).

Type B - Isokinetic Stack Monitoring (3 units): Installed at ventilation stacks of the Waste Treatment Facility, Building Envelope, and third location as specified. These advanced systems feature isokinetic probe sampling with automatic velocity matching to stack flow, temperature compensation, and alarm capabilities to ensure representative sampling in accordance with international standards ISO 2889 and ISO 10780 (specifications per FT-3).

All fixed aerosol sampling systems include automatic filter changers (minimum 40 filters), integrated detection systems with real-time spectrometric analysis, AI-assisted nuclide identification, and automatic Radon/Thoron compensation. Systems achieve minimum detectable activities of ≤0.1 Bq/m³ for beta global (1-hour integration) and comply with IEC 60579, IEC 60761-2, IEC 61172, and IEC 61578 standards.

Liquid Discharge Monitoring

Liquid discharges to the environment will be monitored using sampling and laboratory analyses, including radio-chemical analysis.

Gaseous Discharges Monitoring

Gaseous discharges (emissions) to the environment will be monitored using installed aerosol sampling systems that sample the discharged air and collect aerosols on filters that are subsequently analysed (counted) in the laboratory.

The gaseous discharge monitoring system comprises two distinct types of aerosol sampling systems deployed according to monitoring location and regulatory requirements:

Type A Systems (4 units) are deployed in interior locations where open sources are manipulated, including the Waste Treatment Facility (compaction room, liquid storage area, and drying/storage room) and the Long-term Source Storage Facility. These systems provide continuous interior air monitoring with adjustable flow rates, automatic filter changing capabilities, and integrated real-time detection. Detailed specifications are provided in FT-3.

Type B Systems (3 units) are deployed at ventilation stack discharge points including the Waste Treatment Facility main stack and Building Envelope auxiliary ventilation outlet. These advanced systems feature isokinetic probe sampling technology that automatically matches sampling velocity to stack flow conditions, maintains temperature compensation from -10°C to +200°C, and provides automatic alarm generation when isokinetic ratios exceed acceptable limits. This ensures representative sampling in compliance with ISO 2889 and ISO 10780 standards for stack emissions monitoring. Detailed specifications are provided in FT-3.

Both system types include advanced capabilities for real-time spectrometric analysis, AI-assisted nuclide identification, automatic Radon/Thoron compensation, and achieve minimum detectable activities of ≤0.1 Bq/m³ for beta global activity. Systems comply with international standards including IEC 60579, IEC 60761-2, IEC 61172, IEC 61578, and relevant ISO standards.

Measurement frequency includes continuous real-time monitoring through integrated detection systems, with subsequent laboratory analysis of collected filters performed weekly during operational periods and monthly during non-operational periods.

Activities conducted may generate radioactive aerosols and contaminated vapors. The ventilation system will be equipped with filters that retain these radioactive elements. The public authority will establish release limits for gaseous effluents.

Environmental Monitoring

Environmental monitoring will be conducted to monitor and assess the impacts of activities conducted at the Beneficiary site on the environment for normal operating conditions and accidents. The following monitoring, measurements, and analyses are required:

- Laboratory analysis of soil, vegetation, water, etc.

- Laboratory analysis of groundwater and meteorological samples collected at the perimeter of the Beneficiary site.

- Routine measurement of gamma dose rates and airborne contamination levels around facilities on the Beneficiary site.

- Routine measurement of gamma dose rates and airborne contamination levels at representative points inside and outside the Beneficiary site.

- Measurement of gamma radiation doses over fixed periods at various points on the fence surrounding the Beneficiary site using thermos-luminescence dosimeters (TLDs) suitable for environmental monitoring.

- Canisters placed inside the Beneficiary site for collection of wet and dry depositions and its analyses in a laboratory.

Seven (7) Fixed Air Sampling Systems for environmental monitoring will be deployed at strategic locations on and around the site. These advanced systems integrate radiological and meteorological monitoring capabilities in a single unit. System locations include: near the underground RADON repository, long-term source storage facility area, intermediate storage facility area, site boundary toward Bubuieci locality, Waste Treatment Facility area near the surface water collection pond, and two additional perimeter locations (exact placement to be determined by Beneficiary due to off-site approval requirements). Detailed specifications are provided in FT-4.

Each environmental monitoring system includes:

Integrated Gamma Spectrometric Chain: LaBr₃ scintillation detector (2" × 2") with measurement range 10⁻² to 10⁴ Bq/m³, energy range 30 keV to 3 MeV, and resolution ≤3.5% FWHM at Cs-137. The integrated gamma spectrometry provides real-time nuclide identification capability directly at the monitoring location.

Air Sampling Specifications: Adjustable flow rate 40-120 m³/h, filter diameter 240mm with ≥99.8% efficiency for particles ≥0.3 μm, automatic filter changer with minimum 20-filter capacity for extended unattended operation, and IP54 minimum protection rating for outdoor installation.

Integrated Meteorological Station: Each system includes sensors for ambient temperature, relative humidity, atmospheric pressure, wind speed and direction, and precipitation. This integrated approach correlates radiological measurements with meteorological conditions for atmospheric dispersion modeling.

Measurement frequency includes continuous real-time gamma spectrometric monitoring with data updates at regular intervals, supplemented by weekly laboratory analysis of collected filters (gamma spectrometry and alpha/beta gross counting). All data is integrated into the central Radiological Monitoring System (RMS).

Systems comply with IEC 60846:2009, CE requirements (2014/30/EU and 2014/35/EU), and relevant environmental monitoring standards.

Data Recording

The information provided by installed and mobile/portable equipment relating to the ERMS need to be integrated into a Radiological Data Acquisition, Processing and Management System (RMS), which is to be installed in the Dosimetry Room of the Waste Treatment building.

The Radiological Data Acquisition, Processing and Management System (RMS) is an enterprise-grade system designed to integrate data from all ERMS components and provide comprehensive monitoring, alarming, data management, and reporting capabilities. Detailed specifications are provided in FT-6.

System Capacity and Architecture: The RMS is designed to manage a minimum of 100 monitoring stations as baseline implementation, with scalability to minimum 150 stations without major infrastructure modifications. The system employs a centralized client-server architecture with web-based access, redundant design with failover capabilities, and modular structure permitting future expansion.

Data Acquisition and Management: The system supports all monitoring stations with user-configurable polling intervals (minimum 10 minutes in normal mode), automatic switching to emergency mode with 1-minute polling capability, multi-channel communication support (Fiber Optic, LAN, 5G, 4G/LTE), automatic data validation and quality control, and time synchronization accuracy within ±1 second. Data processing includes real-time validation, statistical analysis, trend analysis, anomaly detection, and automatic correction factors.

Alarm Management: Multi-level alarm system with configurable thresholds per station and parameter, alarm levels (Warning and Alert), notification through system alerts and audio-visual indicators (optional email and SMS), alarm confirmation and escalation procedures, complete alarm history logging, and response time <30 seconds from detection to notification.

User Interface and Display: multi-language support (Romanian, Russian, English minimum), role-based access control with minimum 5 user privilege levels, concurrent user support (minimum 20), session management with audit logging, and GIS integration with interactive mapping showing real-time station status and color-coded radiation levels.

Data Exchange and Compliance: Mandatory support for EURDEP 2.0 format (European Radiological Data Exchange Platform) and ANSI N42.42 (radiation detector data format), with optional support for IRIX format and RESTful API for third-party integration. The system complies with IEC 61017 (Radiation protection instrumentation), ISO/IEC 27001 (Information security management), IAEA Safety Standards Series No. GSG-16, EU Council Decision 87/600/Euratom, and Law nr. 132/2012 (Republic of Moldova).

Performance Requirements: System uptime 99.5% annual availability, data latency <5 seconds (normal mode) and <2 seconds (emergency mode), database query response <3 seconds, report generation <30 seconds for daily reports, data retention minimum 10 years online storage, and backup frequency of incremental daily with full weekly.

Hardware Components: Complete hardware package includes central server with enterprise-grade specifications, minimum 2 professional workstations with dedicated displays, 42U server rack with UPS (3000VA minimum, 15-minute runtime), managed network switch, network-enabled color printer, and NAS backup solution. Complete specifications provided in FT-6.

Security: Comprehensive security including multi-factor authentication support, password complexity enforcement, session timeout controls, AES-256 encryption for data at rest, TLS 1.3 for transmission, comprehensive audit logging, and GDPR-compliant data handling.

Integrated Systems: The RMS will manage and display data from individual radiation dose measurements, workplace radiation field measurements, and all environmental monitoring locations. Direct real-time integration includes: hand, foot, and clothing contamination monitors (4 units), fixed gamma area monitors (13 detectors + 11 display units), fixed aerosol sampling systems (7 units with complete spectrometric data), and fixed environmental air sampling systems (7 units with integrated gamma spectrometry and meteorological data).

Training and Support: Structured training program includes Administrator Training (5 days, 3-5 personnel), Operator Training (3 days, 5-10 personnel), and Maintenance Training (2 days, 2-3 personnel), with all materials provided in Romanian and English. Technical support includes minimum 24-month warranty, 8×5 support availability, defined response times (Critical: 2 hours, Major: 4 hours, Minor: 24 hours), remote support capability, and on-site support within 48 hours when necessary.

Testing and Acceptance: Factory Acceptance Test (FAT) includes hardware functionality verification, software installation and configuration, communication testing, and performance benchmarking. Site Acceptance Test (SAT) includes end-to-end system functionality, integration with minimum 50 monitoring stations, emergency mode simulation, alarm system verification, 72-hour continuous operation test, and performance criteria verification.

Electrical Supply System

Electrical Supply System (ESS) supplies electrical power to the environmental and radiation monitoring system at the Moldavian national radioactive waste management site. The ESS has been designed to supply electrical power to the following work areas:

- Treatment building.

- Storage building for radiation sources (long-term).

- Containment to be built over the Radon-type facility.

- Sanitary gate located between the supervised area and the controlled area.

- Beneficiary site (at selected points).

Technical Documentation

The technical documentation of the Storage Facility and ERMS that will be provided to the wining Bidder are defined in Table 3 and Table 4 respectively.

Table 3: Technical Documentation of the Storage Facility.

| TITLE | DOCUMENT NO. | LANGUAGE |
| --- | --- | --- |
| Bill of Quantities | DRMO-1045521-PTh/A-LCL-2 | RO |
| Final Report for the Design of a Storage Facility for Radioactive Waste in Moldova (REDACTED). | DRMO-1045521-PTh/TP-RAP-2 | EN |
| General Technical Report | DRMO-1045521-PTh-TP-MT | RO |
| Technical Project – General Layout and External Network (Provided for Information Purposes) | DRMO-1045521-PTh-PG | RO |
| Technical Project – Architecture | DRMO-1045521-PTh-AR | RO |
| Technical Project – Civil Design | DRMO-1045521-PTh-R | RO |
| Technical Project – Crane and lifting device | DRMO-1045521-PTh-IR | RO |
| Technical Project – Mechanical Ventilation System | DRMO-1045521-PTh_V | RO |
| Technical Project – Water Supply and Potentially Radioactive Water Drainage System | DRMO-1045521-PTh-S | RO |
| Technical Project – Potentially Radioactive Effluent Drainage System | DRMO-1045521-PTh-RA | RO |
| Technical Project – Fire Protection System | DRMO-1045521-PTh-SI | RO |
| Technical Project – Electrical Supply System | DRMO-1045521-PTh-E | RO |
| Technical Project – Automation System | DRMO-1045521-PTh-A | RO |
| Technical Project – Low Voltage Systems | DRMO-1045521-PTh-CSL | RO |
| Technical Project – Radiation Monitoring System | DRMO-1045521-PTh_DOZ_REV.1 | RO |

Table 4: Technical Documentation of the ERMS.

| TITLE | DOCUMENT NO. | LANGUAGE |
| --- | --- | --- |
| GENERAL TECHNICAL DOCUMENTS |  |  |  |
| General Description Report | SMMO-1045522-PTh/DOZ-MP | EN |
| Final Report for Development of Detailed Technical Design for ERMS (REDACTED). | SSMO-1045522-PTh/DOZ-RAP-2 | EN |
| Specification for the procurement, installation and commissioning of ERMS | SMMO-1045522-LIC | RO |
| ELECTRICAL SUPPLY SYSTEM (ESS): DETAILED TECHNICAL DESIGN - SMMO-1045522-PTh/E |  |  |  |
| Technical Report for the Detailed Technical Design of Electrical Supply. | SMMO-1045522-PThE-MT | RO |
| Specifications for Procurement and Installation. Appended to this document are: - Work quality control program in the decisive execution phases (SMMO-1045522-PTh/EPFD); - Preliminary measurements Electrical System (Power) (SMMO-1045522-PTh/E-AM); - Bill of Quantities (SMMO-1045522-PTh/E-LCL-1); - Technical Fisch 1, 2, 3 (SMMO-1045522-PTh/E-FT-1/2/3). | SMMO-1045522-PThE-CS | RO |
| ESS Drawings: |  |  |
| Electrical Single Line Diagram TD1: Conditioning Facility for RW. | SMMO-1045522-PThE-OL-1 | RO |
| Electrical Single Line Diagram TD3: Containment building. | SMMO-1045522-PThE-OL-2 | RO |
| Electrical Single Line Diagram TD2: Storage Facility for DSRS. | SMMO-1045522-PThE-OL-3 | RO |
| Electrical Single Line Diagram TD4: Sanitary Gate. | SMMO-1045522-PThE-OL-4 | RO |
| Electrical power installation: Conditioning Facility. | SMMO-1045522-PThE-SK-1 | RO |
| Electrical power installation: Storage Facility for DSRS. | SMMO-1045522-PThE-SK-2 | RO |
| Electrical power installation: Containment building. | SMMO-1045522-PThE-SK-3 | RO |
| General location: Electrical installations. | SMMO-1045522-PThE-SK-4 | RO |
| Electrical power installation: Sanitary Gate. | SMMO-1045522-PThE-SK-5 | RO |
| Cable log. | SMMO-1045522-PThE-CL | RO |
| ENVIRONMENTAL AND RADIATION MONITORING SYSTEM: DETAILED TECHNICAL DESIGN - SMMO-1045522-PTh/DOZ, REV.0. |  |  |  |
| Technical Report for Detailed Technical Design of Environmental and Radiation Monitoring System. | RMS SMMO-1045522-PTh_DOZ-MT | RO |
| System of enquiring, processing and management of radiation protection data. Block diagram. | RMS SMMO-1045522-PTh_DOZ-BDG-1 | RO |
| Specifications for Procurement and Installation. | SMMO-1045522-PTh_DOZ-CS | RO |
| RMS Drawings: |  |  |
| Conditioning Facility of radioactive waste. General location: SG, DAU, RMS, HFC, ARB. | SMMO-1045522-PTh_DOZ-SK1 | RO |
| Storage Facility for DSRS: General locations of gamma monitors and aerosol sampling system at the exhaust pipe. | SMMO-1045522-PTh_DOZ-SK2 | RO |
| Containment facility. General location: SG, DAU, HFC, RAB. | SMMO-1045522-PTh_DOZ-SK3 | RO |
| Sitewide. Location general: Sanitary gate, AIR, TLD, HFC, DEP. | SMMO-1045522-PTh_DOZ-SK4 | RO |
| Sanitary gate scheme. | SMMO-1045522-PTh_DOZ-SK5 | RO |
| General Arrangement | DRMO-1045521-PTh/DOZ-GA-1 | RO |

This technical documentation is the Intellectual Property of the Beneficiary. Accordingly, it will only be made available to the winning Bidder, vetted by the Beneficiary and local authorities, and have submitted a Non-Disclosure Agreement. All bidders may get familiarized with the site and the above technical designs’ documentation during Site visit.

Contractor’s Qualifications

Technical and Human Resources

- The Contractor shall have adequate technical equipment required to implement the work.

- The Contractor shall have access to the necessary qualified human resources to implement the work.

- Key personnel involved in the establishment of the Storage Facility (Section 5.2.2) shall have at least 10 years’ experience in all activities associated with the work.

- Key personnel involved in the establishment of the ERMS (Section 5.2.3) shall have at least 5 years’ experience in all activities associated with the work.

Personnel

- Key personnel shall be qualified, experienced, and possess the necessary accreditations, certificates and permits required to implement the work.

- Key personnel for the establishment of the Storage Facility are:

  - Project Manager.

  - Construction Manager/Foreman.

  - Specialists, in-house or sub-contractors:

    - Lead Designer.

    - Licensing/Authorisation Lead.

    - Construction:

      - Civil and industrial construction.

      - Road construction.

      - Water supply and sewerage installations and networks.

      - Electrical installations and networks.

      - Earthworks, execution and dismantling of constructions, building protection works, construction finishing works.

      - Telecommunication installations and networks.

- Key personnel for the establishment of the ERMS will minimally be:

  - Certified Electricians (HV and LV).

  - Specialists, in-house or sub-contractors:

    - Instrumentation Specialist.

    - IT/Network Specialist.

Quality of Project Management/Certificates

- The Contractor shall possess and maintain a valid quality assurance program. At any time during the implementation of the work and upon request by the Beneficiary, the Contractor shall provide evidence that an appropriate QA/QC system has been suitably implemented.

- The quality certificates shall include the following:

  - Quality Certificates and/or other similar certificates, accreditations, awards and citations received by the Bidder, which shall minimally include the following:

    - ISO 45001:2018 Certificate "Occupational Health and Safety Management System"

    - ISO 9001:2015 Certificate "Quality Management System"

    - ISO/IEC 27001:2018 Certificate "Information Security Management System"

  - Environmental Compliance Certificates: Accreditations, Markings/Labels, and other evidence of the Bidder’s practices that contribute to the ecological sustainability and reduction of adverse environmental impact (e.g., use of non-toxic substances, recycled raw materials, energy-efficient equipment, reduced carbon emission, etc.), either in its business practices or in the goods it manufactures. Minimum to include Environmental Management System SR EN ISO 14001:2015.

  - Certificate of Registration of the Business, including Articles of Incorporation, or equivalent document if Bidder is not a corporation.

  - Notice for participation in Public tenders for works in the field of constructions and installations issued by Agency for Technical Supervision of Ministry of Infrastructure and Regional development of Republic of Moldova.

  - Quality Certificates (ISO or CE) for the main materials and equipment/instruments, as applicable, in accordance with the technical specifications/datasheets.

  - Other similar certificates, accreditations, awards and citations received by the Bidder, if any.

Project Tasks and Deliverables

The proposed breakdown of the Scope of Work (SOW) is as follows:

- Task 1: Project Planning and Management.

- Task 2: Design Verification and Completion.

- Task 3: Support Beneficiary to obtain Construction Authorisation.

- Task 4: Establishment.

- Task 5: Project Closure.

These tasks are defined and described in more detail in the following subsections.

Task 1: Project Planning and Management

The purpose of Task 1 is to define and establish the project organisation and management arrangements that will govern implementation of the work. In this task, the Contractor shall:

- Establish the Project Team and define each team member’s roles, responsibilities, and authorities.

- Organise the Project Working Group composed of the Contractor’s, Beneficiary's and other experts, and define their individual functions, duties, and rules of interaction / communication protocols.

- Develop a Project Quality Plan for the project that will ensure the quality of all activities, deliverables, materials, and products associated with the work. All relevant systems, processes, and procedures, as well as outputs (including records) that demonstrate conformance with the defined quality requirements and standards need to be specified (see template provided as Annexure 8.

- Develop a detailed Project Plan and schedule for the project. This plan will serve as basis for progress reporting to internal and external stakeholders of the project and needs to be suitably detailed to be implemented to deliver the scope of work of this contract. The Project Plan shall also include:

- A Procurement Plan for all items/equipment/instruments of the Storage Facility and ERMS that addresses the selection and qualification of suppliers, the process/procedure for procurement, the inspection, receipt, and acceptance of items/equipment, the management of procurement and item-specific documentation for operations, maintenance, and record keeping.

- A Construction and Commissioning Plan for the Storage Facility and ERMS covering the construction, installation, functional testing, commissioning and other verification and validation activities to ensure conformance to the final design specifications, as well as the subsequent qualification / certification / accreditation of the ERMS (as needed).

- Develop a detailed specification for the Radiological Data Acquisition, Processing and Management System (RMS) (Section 3.6).

All task activities and deliverables need to be completed in accordance with the approved Project Plan and Project Quality Plan.

Task 2: Design Verification and Completion

The objectives of Task 2 are to verify, integrate, and finalise the supplied design package (Table 3) of the Storage Facility. In this task, the Contractor shall:

- Perform a gap analysis by reviewing the supplied design package and develop a Gap Analysis Report. The review needs to be performed at the detail design level to assess the readiness to establish (i.e., procure, manufacture, construct, install, and commission) the Storage Facility in the Republic of Moldova. The Radiation Monitoring System (Section 2.3.8) has been finalised and only needs to be reviewed from an integration/interface perspective.

- Based on the gap analysis findings, finalise the detailed design package of the facility in accordance with the project requirements established in Task 1, the designs (Annexures 3 and 4), and the legal and technical requirements of the Republic of Moldova. The final design package has to ensure that all Structures, Systems, and Components (SSC) are suitably integrated and specified for establishment in accordance with Moldovan legislation. Design changes need to be managed in accordance with certified change management processes (e.g., ISO 9001:2015) and be authorised by the Beneficiary.

- Have the final design package verified for establishment by an independent organisation or certified external experts (to be approved by the Beneficiary during Task 1). This verification shall also assess compliance with all relevant laws and regulations, including authorisation by Moldovan authorities, and whether the design specifications are complete and according to Moldovan standards and requirements.

- If needed following the independent review, update the final design package and the Construction and Commissioning Plan to ensure nuclear facility construction readiness and regulatory compliance.

As before, all task activities and deliverables need to be completed in accordance with the approved Project Plan and Project Quality Plan.

Task 3: Support Beneficiary to Obtain Construction Authorisation

The objective of Task 3 is to assist the Beneficiary in obtaining the construction authorisations from NARNRA and other authorities required by Moldovan law. The Beneficiary is responsible for obtaining these authorisations using the final design package and construction and commissioning planning-related deliverables developed by the Contractor. In this task, the Contractor shall:

- Ensure that the design (cf. 6.2.2/6.2.4) and construction/commissioning (cf. 6.2.4/6.2.4) documentation required by the authorities have been provided to the Beneficiary for submission to the authorities in support of the request for construction authorisation. Documentation must meet nuclear facility construction authorization requirements and demonstrate compliance with nuclear safety standards.

- If required, draft responses to technical questions raised by the authorities related to the design and construction/commissioning documentation (see 6.3.1). Provide additional information requested by authorities related to nuclear facility construction requirements.

- If required, provide additional information requested by the authorities related to the design and construction/commissioning documentation (see 6.3.1).

- If required by the authorities (cf. 6.3.2 and 6.3.3), update the design and construction/commissioning documentation (see 6.3.1).

Note that NARNRA typically responds to submissions/requests within 3 months. Should NARNRA find that the submission/request does not comply with the regulatory requirements or international requirements and best practices (such as the IAEA Safety Standards), the submission/request will need to be updated and re-submitted, at which point another 3-month review cycle is initiated. Therefore, it is recommended that every effort be made to ensure that the initial submission/request is of high quality and complies with all relevant requirements.

As before, all task activities and deliverables need to be completed in accordance with the approved Project Plan and Project Quality Plan.

Task 4: Establishment

The objectives of Task 4 are (a) to procure the items and equipment/instruments of the Storage Facility and ERMS, (b) to establish the Storage Facility, (c) to install the ERMS, and (d) to commission and verify and validate conformance of the Storage Facility and ERMS with the final design specifications. In this task, the Contractor shall:

- Procure the items and equipment/instruments required to establish the Storage Facility and ERMS in accordance with the Procurement Plan and perform site acceptance and verification of compliance with the design specifications (e.g., datasheets and technical specifications). All necessary documentation for completing the Beneficiary’s inventory lists and asset management system documentation shall also be provided to the Beneficiary.

- Prepare the site for construction of the Storage Facility and installation of the ERMS in liaison and cooperation with the Beneficiary, who is responsible for all earth works related to the establishment of the Storage Facility (DRMO-1045521-PTh-PG). In this regard:

- The Contractor is not responsible for any earth works required for construction of the Storage Facility (i.e., as defined/specified in the Construction and Commissioning Plan).

- The Contractor is responsible for other site preparatory activities required for construction of the Storage Facility and installation of the ERMS (i.e., as defined/specified in the Construction and Commissioning Plan).

- Establish the Storage Facility and install the ERMS in accordance with the Construction and Commissioning Plan. All design changes necessitated during construction/installation need to be managed in accordance with certified change management processes (e.g., ISO 9001:2015) and be authorised by the Beneficiary.

- For each stage of construction defined in the Construction and Commissioning Plan, the Contractor is required to:

- Prepare and provide a progress report detailing the works completed in this stage.

- Prepare and provide a Certificate of Completion of Works in accordance with the provisions of the Project Quality Plan and/or Construction and Commissioning Plan.

- Prepare and provide a copy of the on-site Building Construction Manual.

- Ensure all laboratory tests are performed and certificates are provided (if any).

- Prepare and provide Certificates of Quality and Conformity of materials used on site.

- Issue warranty certificates for installed equipment (if any).

- Prepare and provide the Bill of Works for the work completed in this stage.

- Prepare and provide an interim payment order for the volume of work executed in this stage (as approved by the Beneficiary in Task 1, also see Table 5).

- Provide all necessary information and documentation to the Beneficiary to include in the Facility in the Cadastre Register in accordance with Moldovan Legislation.

- Test and commission the Storage Facility and ERMS in accordance with the Construction and Commissioning Plan and perform all necessary functional tests and commissioning (validation) activities to verify and validate conformance with the final design specifications. This shall minimally include the following:

- For each category of goods, the Contractor in cooperation with the Beneficiary, will establish the necessary tests in order to verify the correctness of the connection of the equipment and their compliance with the predetermined tasks. These tests will be carried out according to a test schedule, and for each test a report confirming the passing of the tests will be drawn up.

- The installation and commissioning of the goods will be carried out by the Contractor in accordance with the schedule elaborated and coordinated with the Beneficiary.

- After establishing the Storage Facility, perform the final topographic measurements and finalise the GIS model / topographical drawings.

- Obtain all necessary Certificates of Conformance (CoC) and other certifications/accreditations defined in the Construction and Commissioning Plan and/or Project Quality Plan.

- Develop all necessary construction and commissioning documentation specified in the Construction and Commissioning Plan and Project Quality Plan (e.g., As-Built drawings, updated design documentation, Construction Report, Commissioning Report, Change/Configuration Management Records, functional testing reports, verification and validation reports, other commissioning reports, etc.).

- Develop all manuals and procedures required to operate, maintain and calibrate (as applicable) the Storage Facility and ERMS subsystems and equipment/instruments, excluding the IMP.

- Train and certify Beneficiary staff to operate, maintain and calibrate (as applicable) the Storage Facility and ERMS subsystems and equipment/instruments, excluding the IMP.

- Obtain the required qualification / certification / accreditation of the ERMS subsystems and/or equipment/instruments.

All task activities and deliverables need to be completed in accordance with the Procurement Plan, Construction and Commissioning Plan, relevant provisions of the Construction Authorisation, the Project Plan and the Project Quality Plan.

Task 5: Project Closure

The objectives of Task 5 are the formal hand-over of the Storage Facility and ERMS to the Beneficiary and to close-out the project upon completion of all contractual requirements. In this task, the Contractor shall:

- Prepare a Final Report for the project.

- Ensure that all documentation, deliverables, products, and materials associated with the contract are provided to the Beneficiary. Design documentation and drawings need to be provided in hard copy and soft copy. Simulations, design analyses, drawings, etc. need to be provided in the original file format (e.g., CAD, AutoCAD, etc.), while other documentation associated with the contract need to be provided in MS Word and pdf formats.

- Ensure that all non-conformances and change/configuration management reports are closed-out.

- Account for defect liability for a period of 12 months, which shall minimally amount to 10 % of the establishment cost (Task 4).

- Manage defect liability in accordance with the provisions of the contract. This includes the following:

  - Prepare a report on defects identified during the warranty period (if any).

  - Provide laboratory tests results and certificates (if any).

  - Provide certificate of elimination of defects.

  - Prepare and provide a Certificate of Final Completion (delivered after Defect Liability Period/warranty period).

  - Prepare and provide a Claim for the Release of the Performance Security on two occasions during the Defect Liability Period of 12 months.

Indicative Project Timeline and Conisiderations

#### CRITICAL FUNDING NOTICE

This project is financed under EU SIDA funding with the following non-negotiable constraints:

- EU SIDA Project End Date: 27 July 2027

- Required Construction Contract Finalization: By end of June 2027

- All works must be completed and closed within these constraints

Bidder Timeline Proposal Requirements

Bidders shall propose their own realistic timeline with the following mandatory elements:

| TASK | BIDDER TO PROPOSE | MANDATORY INFORMATION REQUIRED |
| --- | --- | --- |
| Task 1: Planning and Management | Duration and completion date | • Mobilization timeframe • Team deployment schedule • Nuclear facility planning standards implementation |
| Task 2: Design Verification and Completion | Duration and completion date | • Design review timeline • Regulatory compliance verification period • Independent expert review schedule |
| Task 3: Construction Authorization | Duration and completion date | • NARNRA submission preparation • Expected approval timeframe • Contingency for regulatory iterations |
| Task 4: Comprehensive Establishment | Duration and completion date | CRITICAL: Must clearly state: • Construction start date • Construction completion date • Testing and commissioning schedule |
| Task 5: Project Closure | Duration and completion date | CRITICAL: Must complete before end June 2027 • Handover schedule • Defect liability period management |

#### Mandatory Timeline Information

Bidders must explicitly provide in their technical proposal:

- Proposed Construction Completion Date (end of Task 4)

- Proposed Contract Closure Date (end of Task 5) - must be before end June 2027

- Total project duration from contract signature

- Critical path analysis showing:

  - Dependencies between tasks

  - Float/buffer time for each activity

  - Risk mitigation measures for schedule delays

- Resource deployment schedule showing:

  - Personnel mobilization timeline

  - Equipment delivery schedule

  - Subcontractor engagement periods

- Monthly milestone schedule for progress monitoring

*Note: Timeline includes regulatory contingency buffers and extended establishment period to accommodate comprehensive project delivery responsibility.

### 7.2 Payment Structure Framework

Bidders shall propose payment schedules that align with enhanced project milestones while ensuring adequate cash flow for comprehensive nuclear facility establishment. Payment proposals must address:

a. Milestone-Based Payment Structure

- Percentage of total contract value paid at each major nuclear facility establishment milestone

- Alignment of payments with nuclear facility construction progress and regulatory compliance achievements

- Integration of payment milestones with nuclear facility commissioning and operational readiness verification

b. Risk Management and Security Provisions

- Retention amounts and release conditions appropriate for nuclear facility construction

- Performance security arrangements that address nuclear facility establishment risks

- Defect liability provisions enhanced for nuclear facility operational requirements

c. Nuclear Facility Specific Considerations

- Payment adjustments for nuclear regulatory approval delays beyond contractor control

- Provisions for nuclear facility-specific testing and commissioning requirements

- Integration of payment structure with existing site operational coordination requirements

At the end of each task, the Contractor shall prepare a task report and submit it to the Beneficiary for approval. The approval shall be in writing. In case the Beneficiary has comments on a task report, these must be addressed within fifteen (15) working days.

The Contractor shall also prepare quarterly progress reports and submit it to the Beneficiary for approval. The approval shall be in writing. As before, in case the Beneficiary has comments on this report, these must be addressed within fifteen (10) working days.

General Requirements of the Contractor

### 8.1 Comprehensive Nuclear Facility Delivery Requirements

8.1.1 Complete Project Infrastructure and Delivery Provide all necessary infrastructure, systems, instruments, equipment, tools, materials, and human resources required to establish the complete Storage Facility and ERMS and complete all aspects of the scope of work. This includes all earthworks equipment, site preparation resources, construction materials, nuclear facility-qualified equipment, and specialized nuclear facility construction expertise.

8.1.2 Nuclear Facility Establishment Standards Establish all infrastructure, systems, instruments, equipment, and tools according to nuclear facility construction standards and regulatory requirements, with appropriate integration with existing nuclear site infrastructure and operations.

8.1.3 Nuclear Facility Documentation Standards Provide two complete sets of operating and servicing manuals and technical drawings meeting nuclear facility documentation standards. All documentation must be suitable for nuclear facility operations and regulatory compliance requirements.

### 8.2 Nuclear Facility Language and Training Requirements

8.2.1 Documentation Language Requirements Provide all deliverables in Romanian language with nuclear facility terminology accuracy. Provide the following reports additionally in English language:

- All task reports and quarterly progress reports

- For Task 1, the Project Quality Plan and Project Plan

- For Task 4, the establishment progress reports

- For Task 5, the Final Report

8.2.2 Nuclear Facility Training Requirements Conduct all training activities and provide training materials in Romanian language according to nuclear facility training standards. Training must address nuclear safety requirements, radiological protection protocols, and coordination with existing site operations.

### 8.3 Nuclear Site Coordination and Safety Requirements

8.3.1 Nuclear Site Coordination Protocol Agree with the Beneficiary, prior to commencement of works, on exact locations and coordination protocols for Storage Facility and ERMS establishment that minimize disruption to existing nuclear site operations while maintaining nuclear safety and security requirements.

8.3.2 Nuclear Facility Safety and Equipment Requirements Inform the Beneficiary in a timely manner of any site requirements for safe deployment of machinery, equipment, and tools in the nuclear facility environment. No construction activities shall commence before Construction Authorization and Beneficiary permission, with appropriate coordination with nuclear site safety management.

8.3.3 Nuclear Facility Waste and Site Management Remove all waste, tools, and equipment from the nuclear site following completion of works according to nuclear facility waste management protocols and coordination with existing site waste management programs.

### 8.4 Nuclear Regulatory and Standards Compliance

8.4.1 Nuclear Industry Standards Compliance Comply with all relevant national and international nuclear facility requirements and standards in implementing the scope of work, including coordination with existing nuclear site regulatory compliance programs.

8.4.2 Nuclear Facility Change Management During establishment of the Storage Facility and ERMS, perform any design changes according to certified change management processes appropriate for nuclear facilities and obtain Beneficiary approval for all changes affecting nuclear facility operations or regulatory compliance.

8.4.3 Nuclear Facility Specification Compliance Establish the Storage Facility and ERMS according to final design specifications and nuclear facility construction standards, with appropriate integration with existing nuclear site infrastructure and coordination with ongoing nuclear facility operations.

### 8.5 Nuclear Site Operational Requirements

8.5.1 Nuclear Facility Quantities and Specifications Provide items in quantities specified in the Bill of Quantities with nuclear facility quality standards and appropriate integration with existing nuclear site operations and management systems.

8.5.2 Nuclear Site Rules and Protocols Compliance Comply with all relevant nuclear site requirements and rules including radiation protection, nuclear security, waste management, and coordination with existing nuclear site operations throughout the establishment period.

8.5.3 Radiological Work Program Implementation Construction and installation work will be performed in a Controlled Area where nuclear facility-specific rules must be complied with during establishment. At its own expense, implement a radiation protection program for workers according to Beneficiary's specifications and requirements, coordinated with the Beneficiary and relevant nuclear regulatory authorities.

8.5.4 Nuclear Site Waste Management Coordination Manage waste generated on site according to Beneficiary's specifications and requirements, coordinated with the Beneficiary and relevant authorities. Waste generated on site may be radioactively contaminated and must be managed according to nuclear facility waste management protocols.

8.5.5 Nuclear Site Utility Management Provide and install meters for electricity and water consumption. Pay for consumption according to existing fees approved by the Beneficiary's suppliers, with coordination with existing nuclear site utility management systems.

Quality Control and Quality Assurance Requirements

### 9.1 Nuclear Facility Quality Management Standards

9.1.1 Nuclear Industry Professional Standards Carry out all works in a thorough, efficient, and professional manner according to nuclear facility construction standards and nuclear industry best practices, in accordance with contractual and nuclear facility project requirements.

9.1.2 Nuclear Facility Equipment and Personnel Standards Ensure the use of suitable and efficient equipment and procedures meeting nuclear facility standards, and deploy professional, qualified, and experienced staff with nuclear facility expertise to execute the scope of work.

### 9.2 Nuclear Facility Goods and Installation Standards

9.2.1 Nuclear Facility Equipment Quality Requirements Ensure that goods (items/equipment/instruments) delivered are new with certificates of conformity and warranty meeting nuclear facility standards. Goods shall comply with technical specifications of the Storage Facility (Annexures 3 and 4) and the ERMS (Annexures 5 - 7), including updated specifications per technical datasheets FT-1 through FT-17, and nuclear facility quality requirements with appropriate nuclear facility traceability documentation.

9.2.2 Storage Facility Nuclear Integration Standards Ensure that Storage Facility goods are installed and harmoniously integrated into the facility structure and connected to all networks and systems necessary for nuclear facility operation. Ensure stable and correct operation of all Storage Facility systems according to nuclear facility operational standards and coordination with existing nuclear site operations.

9.2.3 ERMS Nuclear Site Integration Standards Ensure that ERMS goods are suitably installed at their nuclear site locations and connected to all networks and systems necessary for operation according to nuclear facility standards. This includes proper integration of Type A and Type B aerosol sampling systems per their respective installation requirements (FT-3), environmental monitoring systems with integrated gamma spectrometry and meteorological sensors (FT-4), the comprehensive RMS system with all hardware and software components (FT-6), and the purpose-built sanitary airlock container with all functional zones and safety systems (FT-7). Ensure stable and correct operation of all ERMS systems with appropriate coordination with existing nuclear site monitoring and management systems. Ensure that systems are installed without impacting other nuclear site operations and activities in any unintended manner.

### 9.3 Nuclear Facility Final Reporting Standards

The final report shall contain comprehensive information meeting nuclear facility documentation standards:

- Full record of materials preparation, testing, and verification according to nuclear facility standards

- Complete record of all staff deployed at the nuclear site with nuclear facility qualifications verification

- Details of all work performed, including nuclear facility-specific preparation and coordination activities

- Documentation of problems encountered during establishment and their resolution according to nuclear facility problem-solving protocols

- Verification of nuclear facility operational readiness and integration with existing nuclear site operations

Operational Health and Safety Requirements

- The Beneficiary and the Contractor shall hold a pre-establishment safety meeting to discuss the health, safety, and environmental considerations of the work. The meeting shall include a site visit and discussion of logistical arrangements and health and safety requirements prior to site establishment and the Contractor mobilising equipment to the Beneficiary’s site.

- Throughout the establishment period, the Contractor shall keep the construction/installation areas clean and free of all rubbish and debris.

- The Contractor shall at all times during the establishment period ensure the health and safety of its personnel and other persons at the construction/installation areas through the use of appropriate equipment and procedures.

- The Contractor shall provide the required protective barriers and/or other safety protection measures needed to suitably protect all persons at all times during the establishment period at the construction/installation areas.

- All applicable safety requirements shall be complied with. This includes the national health and safety requirements and those additionally defined by the Beneficiary.

- All incidents/events, including but not limited to safety incidents/events, shall immediately be reported to the Beneficiary. Such incidents/events shall be investigated by the Contractor and Beneficiary to identify root causes and define corrective actions. Corrective action shall be taken and reported.

Environmental Protection

### 11.1 Nuclear Facility Environmental Management Integration

11.1.1 Nuclear Site Environmental Requirements Compliance During establishment of the Storage Facility and ERMS, work according to environmental requirements and guidelines that comply with Moldovan requirements and nuclear facility environmental management standards, coordinated with existing nuclear site environmental management programs.

11.1.2 Nuclear Facility Environmental Monitoring Coordination Adherence to environmental requirements will be monitored by the Beneficiary and appropriate nuclear regulatory authorities according to nuclear facility environmental compliance protocols. Infringements may result in rework and corrective action according to nuclear facility environmental management standards.

11.1.3 Nuclear Site Environmental Protection Standards Take care to avoid harm to the environment in handling and storage of all equipment, tools, materials, rubbish, and debris according to nuclear facility environmental protection standards and coordination with existing nuclear site environmental management systems.

### 11.2 Nuclear Facility Environmental Integration Protocol

11.2.1 Nuclear Site Environmental Compliance Dispose of any toxic materials according to local legislation and nuclear facility environmental management protocols, coordinated with existing nuclear site environmental management programs.

11.2.2 Nuclear Facility Environmental Impact Prevention Comply with all relevant Environmental Protection requirements to ensure surface and sub-surface property and equipment are not damaged and flora and fauna are not adversely impacted, according to nuclear facility environmental protection standards and coordination with existing nuclear site environmental monitoring programs.

11.2.3 Nuclear Site Environmental Training and Awareness Ensure that all personnel are aware of applicable environmental guidelines and consequences of not adhering to them, according to nuclear facility environmental management training standards and coordination with existing nuclear site environmental management programs.

Responsibilities of the Beneficiary

The Beneficiary will:

- Provide access to the Beneficiary site during working hours (8:00 to 15:30, Monday to Friday) with appropriate nuclear site access protocols and coordination with ongoing nuclear facility operations.

- Provide a metered connection point to the existing electrical power system.

- Provide a metered connection point to the existing water supply system.

- Provide the necessary (induction) training for Contractor’s staff involved in onsite establishment works.